{"text_format":"1","workbook":"xlsx","n_sheets":4,"sheets":["Tracé DAH","Liste","Graph DAH","Resultats"],"not_rendered":{"charts":2,"images":0,"macros":1,"external_links":0,"defined_names":74,"comments":0,"pivot_tables":0},"unopened":[{"sheet":"Graph DAH","index":2,"reason":"not_a_worksheet"}],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Tracé DAH","index":0,"n_rows":134,"n_cols":26,"rows_kept":134,"cut":false,"hidden":true,"merged":[]}
["Altitude (m)",0]
[]
["TS","HR","HR","HR","HR","WA 100","WA 80","WA 50","WA 30",null,"WA de ENTH0","WA de ENTH10","WA de ENTH20","WA de ENTH30","WA de ENTH40","WA de ENTH50","WA de ENTH60","WA de ENTH70","WA de ENTH80","WA de ENTH90","WA de ENTH100",null,"v'","w","Ts","HR"]
[-15,100,80,50,30,{"$f":"waCEBTP(altitude,$A4,B4)","v":1.1835973211782618},{"$f":"waCEBTP(altitude,$A4,C4)","v":0.9465176332335602},{"$f":"waCEBTP(altitude,$A4,D4)","v":0.59123613205048242},{"$f":"waCEBTP(altitude,$A4,E4)","v":0.35460685197398095},null,{"$f":"(0-1.007*$A4)/(2500.8+1.826*$A4)*1000","v":6.1069535580433474},{"$f":"(10-1.007*$A4)/(2500.8+1.826*$A4)*1000","v":10.149954920534805},{"$f":"(20-1.007*$A4)/(2500.8+1.826*$A4)*1000","v":14.192956283026264},{"$f":"(30-1.007*$A4)/(2500.8+1.826*$A4)*1000","v":18.235957645517722},{"$f":"(40-1.007*$A4)/(2500.8+1.826*$A4)*1000","v":22.278959008009181},{"$f":"(50-1.007*$A4)/(2500.8+1.826*$A4)*1000","v":26.321960370500644},{"$f":"(60-1.007*$A4)/(2500.8+1.826*$A4)*1000","v":30.3649617329921},{"$f":"(70-1.007*$A4)/(2500.8+1.826*$A4)*1000","v":34.407963095483559},{"$f":"(80-1.007*$A4)/(2500.8+1.826*$A4)*1000","v":38.450964457975019},{"$f":"(90-1.007*$A4)/(2500.8+1.826*$A4)*1000","v":42.493965820466478},{"$f":"(100-1.007*$A4)/(2500.8+1.826*$A4)*1000","v":46.536967182957937},null,0.75,0,{"$f":"W4*ptotz(altitude)/(461.51*(0.622+X4/1000))-273.15","v":-8.4173638100013477},{"$f":"hrbc(altitude,Y4,X4)","v":0}]
[-14.5,100,80,50,30,1.2329440811892285,0.98596438425947408,0.61586165234775447,0.36937070121548266,null,{"$f":"(0-1.007*$A5)/(2500.8+1.826*$A5)*1000","v":5.9012101492004057},{"$f":"(10-1.007*$A5)/(2500.8+1.826*$A5)*1000","v":9.9427196853442315},{"$f":"(20-1.007*$A5)/(2500.8+1.826*$A5)*1000","v":13.984229221488057},{"$f":"(30-1.007*$A5)/(2500.8+1.826*$A5)*1000","v":18.025738757631885},{"$f":"(40-1.007*$A5)/(2500.8+1.826*$A5)*1000","v":22.067248293775709},{"$f":"(50-1.007*$A5)/(2500.8+1.826*$A5)*1000","v":26.108757829919536},{"$f":"(60-1.007*$A5)/(2500.8+1.826*$A5)*1000","v":30.15026736606336},{"$f":"(70-1.007*$A5)/(2500.8+1.826*$A5)*1000","v":34.191776902207181},{"$f":"(80-1.007*$A5)/(2500.8+1.826*$A5)*1000","v":38.233286438351016},{"$f":"(90-1.007*$A5)/(2500.8+1.826*$A5)*1000","v":42.274795974494836},{"$f":"(100-1.007*$A5)/(2500.8+1.826*$A5)*1000","v":46.316305510638664},null,0.75,1.88,{"$f":"W5*ptotz(altitude)/(461.51*(0.622+X5/1000))-273.15","v":-9.2151091392909734},{"$f":"hrbc(altitude,Y5,X5)","v":99.967069280319009}]
[-14,100,80,50,30,1.2841449655107098,1.0268919601446633,0.64141037350939956,0.38468754720317289,null,5.6956185187998223,9.7356373291274032,13.775656139454982,17.815674949782561,21.855693760110142,25.895712570437723,29.935731380765304,33.975750191092885,38.015769001420466,42.055787811748047,46.095806622075621]
[-13.5,100,80,50,30,1.3372613523008714,1.0693492749411828,0.66791269075810289,0.40057555689983865,null,5.4901784989513942,9.5287076827767621,13.567236866602128,17.605766050427494,21.644295234252862,25.68282441807823,29.721353601903594,33.759882785728969,37.79841196955433,41.836941153379691,45.875470337205066,null,"v'","w","Ts","HR"]
[-13,100,80,50,30,1.3923563534218388,1.113386616200853,0.69539984520558129,0.41705339981166295,null,5.2848899220124474,9.3219305774340722,13.358971232855696,17.396011888277318,21.433052543698945,25.470093199120566,29.50713385454219,33.54417450996381,37.581215165385437,41.618255820807065,45.655296476228685,null,0.8,0,{"$f":"W8*ptotz(altitude)/(461.51*(0.622+X8/1000))-273.15","v":9.23147860266522},{"$f":"hrbc(altitude,Y8,X8)","v":0}]
[-12.5,100,80,50,30,1.4494948545839048,1.1590556761948343,0.72390394253317847,0.43414025886716984,null,5.0797526205873726,9.1153058444899546,13.150859068392535,17.186412292295117,21.221965516197699,25.257518740100281,29.293071964002863,33.328625187905445,37.36417841180802,41.399731635710602,45.435284859613184,null,0.8,6.01,{"$f":"W9*ptotz(altitude)/(461.51*(0.622+X9/1000))-273.15","v":6.5291128976573418},{"$f":"hrbc(altitude,Y9,X9)","v":100.04331546934101}]
[-12,100,80,50,30,1.5087435562547338,1.2064095836900905,0.75345797196971576,0.45185584145454644,null,4.87476642752718,8.9088333155834381,12.942900203639695,16.976967091695951,21.011033979752209,25.045100867808468,29.079167755864724,33.113234643920975,37.147301531977234,41.1813684200335,45.215435308089752]
[-11.5,100,80,50,30,1.5701710153509252,1.2555029362935195,0.78409582557050406,0.47022039061858395,null,4.6699311759290349,8.7025128226014896,12.735094469273943,16.767676115946397,20.800257762618852,24.832839409291307,28.865421055963761,32.898002702636212,36.930584349308667,40.963165995981122,44.995747642653576,null,"v'","w","Ts","HR"]
[-11,100,80,50,30,1.633847687730134,1.3063918333750302,0.81585231780158673,0.48925469641852865,null,4.465246699135812,8.4963441976785692,12.527441696221327,16.558539194764084,20.589636693306844,24.6207341918496,28.651831690392356,32.68292918893512,36.714026687477869,40.745124186020632,44.776221684563389,null,0.85,0,{"$f":"W12*ptotz(altitude)/(461.51*(0.622+X12/1000))-273.15","v":26.880321015331788},{"$f":"hrbc(altitude,Y12,X12)","v":0}]
[-10.5,100,80,50,30,1.6998459715028376,1.3591339095813906,0.84876320543347994,0.50898010744819111,null,4.2607128307356419,8.2903272731961728,12.319941715656702,16.349556158117231,20.379170600577758,24.408785043038289,28.43839948549882,32.468013927959355,36.497628370419882,40.527242812880417,44.556857255340944,null,0.85,14.66,{"$f":"W13*ptotz(altitude)/(461.51*(0.622+X13/1000))-273.15","v":19.971697093482135},{"$f":"hrbc(altitude,Y13,X13)","v":100.01543811973953}]
[-10,100,80,50,30,1.7682402511837547,1.4137883689532293,0.8828652077488619,0.52941854251971732,null,4.0563294045614562,8.084461881782369,12.11259435900328,16.140726836224193,20.1688593134451,24.196991790666011,28.225124267886919,32.253256745107834,36.281389222328741,40.309521699549656,44.337654176770563]
[-9.5,100,80,50,30,1.8391069427039168,1.4704160196581764,0.91819602706888326,0.55059250251249336,null,3.8520962546905455,7.878747856311354,11.905399457932161,15.93205105955297,19.958702661173778,23.985354262794583,28.012005864415396,32.038657466036199,36.065309067657012,40.091960669277817,44.118612270898623,null,"v'","w","Ts","HR"]
[-9,100,80,50,30,1.9125245393054184,1.5290793093537614,0.95479436960298547,0.57252508238872291,null,3.648013215444101,7.6731850299030011,11.698356844361902,15.723528658820804,19.748700473279705,23.773872287738602,27.799044102197502,31.824215916656406,35.849387731115307,39.874559545574201,43.899731360033108,null,0.9,0,{"$f":"W16*ptotz(altitude)/(461.51*(0.622+X16/1000))-273.15","v":44.529163427998412},{"$f":"hrbc(altitude,Y16,X16)","v":0}]
[-8.5,100,80,50,30,1.9885736583419706,1.5898423611943524,0.99269996662735827,0.59523998337729345,null,3.444080121386774,7.4677732359224054,11.491466350458037,15.515159464993669,19.538852579529301,23.56254569406493,27.586238808600562,31.609931923136195,35.633625037671827,39.657318152207459,43.681011266743091,null,0.9,28.33,{"$f":"W17*ptotz(altitude)/(461.51*(0.622+X17/1000))-273.15","v":30.690265176471939},{"$f":"hrbc(altitude,Y17,X17)","v":100.03001693076979}]
[-8,100,80,50,30,2.067337089009528,1.6527710104971272,1.0319535959974149,0.61876152532762796,null,3.2402968073262239,7.2625123079794305,11.284727808632638,15.306943309285847,19.329158809939056,23.351374310592263,27.37358981124547,31.39580531189868,35.418020812551887,39.440236313205091,43.462451813858301]
[-7.5,100,80,50,30,2.1488998410324576,1.7179328420827968,1.0725971039999287,0.64311465923530409,null,3.0366631083126765,7.05740207992827,11.078141051543863,15.098880023159458,19.119618994775053,23.140357966390646,27.161096938006235,31.181835909621828,35.202574881237425,39.223313852853011,43.244052824468611]
[-7,100,80,50,30,2.2333491943320181,1.7853972283076072,1.1146734275507648,0.66832497994132134,null,2.8331788596384748,6.8524423858669827,10.871705912095491,14.890969438323999,18.910232964552506,22.929496490781013,26.948760017009523,30.968023543238036,34.987287069466539,39.006550595695053,43.02581412192356]
[-6.5,100,80,50,30,2.3207747497052171,1.8552353678039295,1.1582266167444277,0.69441873900698847,null,2.6298438968376381,6.6476330601370632,10.665422223436487,14.683211386735911,18.701000550035335,22.718789713334758,26.736578876634187,30.754368039933613,34.772157203233036,38.789946366532462,42.807735529831888]
[-6,100,80,50,30,2.4112684805435518,1.9275203249476538,1.2033018577619681,0.72142285776651693,null,2.4266580556854165,6.4429739373229813,10.459289818960546,14.475605700598109,18.491921582235673,22.50823746387324,26.524553345510803,30.540869227148367,34.55718510878593,38.573500990423497,42.589816872061057]
[-5.5,100,80,50,30,2.5049247856226082,2.0023270700714804,1.2499454961441265,0.74936494055951741,null,2.2236211721978494,6.2384648522517452,10.25330853230564,14.268152212359535,18.282995892413432,22.297839572467328,26.312683252521218,30.327526932575115,34.342370612629011,38.357214292682904,42.372057972736798]
[-5,100,80,50,30,2.6018405429950251,2.0797325204441623,1.2982050604369288,0.77827328814571117,null,2.0207330826313274,6.0341056399924549,10.047478197353582,14.060850754714707,18.074223312075834,22.08759586943696,26.10096842679809,30.114340984159217,34.127713541520343,38.141086098881473,42.154458656242603]
[-4.5,100,80,50,30,2.7021151650209996,2.159815582036777,1.3481292862173351,0.80817691130430847,null,1.8179936234821465,5.829896135855857,9.8417986482295685,13.853701160603279,17.865603672976988,21.877506185350697,25.889408697724406,29.901311210098115,33.913213722471824,37.925116234845532,41.937018747219241]
[-4,100,80,50,30,2.80585065457218,2.2426571920981204,1.3997681405069176,0.8391055446206247,null,1.6154026314860739,5.6258361753939035,9.6362697193017333,13.646703263209565,17.657136807117393,21.667570351025226,25.67800389493306,29.688437438840889,33.698870982748723,37.709304526656553,41.719738070564382]
[-3.5,100,80,50,30,2.9131516624466207,2.3283403625624604,1.4531728465819578,0.87108966046266501,null,1.412959943617907,5.4219255943993145,9.430891245180721,13.43985689596213,17.448822546743539,21.457788197524945,25.466753848306354,29.475719499087763,33.484685149869165,37.493650800650578,41.502616451431983]
[-3,100,80,50,30,3.0241255460343366,2.4169502243140153,1.5083959091887829,0.90416048315054665,null,1.2106653970910366,5.2181642289051275,9.2256630607192189,13.233161892533309,17.2406607243474,21.248159556161486,25.255658387975579,29.263157219789669,33.270656051603758,37.278154883417848,41.285653715231945]
[-2.5,100,80,50,30,3.138882429274986,2.5085740723337566,1.5654911401736051,0.93835000332179508,null,1.0085188293570113,5.0145519151842679,9.0205850010115221,13.026618086838777,17.032651172666032,21.038684258493287,25.044717344320546,29.050750430147801,33.056783515975056,37.062816601802318,41.068849687629566]
[-2,100,80,50,30,3.2575352639512754,2.6033014117553974,1.6245136845366108,0.97369099249571622,null,0.80652007810510218,4.811088489749106,8.8156569013931101,12.820225313037113,16.824793724681115,20.82936213632512,24.833930547969121,28.838498959613123,32.843067371257128,36.847635782901129,40.852204194545131]
[-1.5,100,80,50,30,3.3801998923638616,2.7012240048587821,1.6855200469205336,1.0102170178402237,null,0.60466898126186663,4.60777378935102,8.6108785974401751,12.613983405529329,16.617088213618484,20.620193021707635,24.62329782979679,28.626402637885942,32.629507445975094,36.632612254064249,40.635717062153404]
[-1,100,80,50,30,3.5069951114357951,2.8024359190302595,1.7485681185444668,1.0479624571446899,null,0.40296537699071694,4.404607650979961,8.4062499249692078,12.407892198958452,16.409534472947694,20.411176746936942,24.412819020926186,28.414461294915434,32.416103568904674,36.417745842893922,40.419388116883169]
[-0.5,100,80,50,30,3.638042738296952,2.9070335757211185,1.8137172045942169,1.086962514002578,null,0.20140910369148682,4.2015899118640156,8.2017707200365457,12.201951528209074,16.202132336381606,20.202313144554132,24.202493952726662,28.202674760899193,32.202855569071723,36.203036377244253,40.203217185416776]
[0,100,80,50,30,3.7734676774013964,3.0151158004366896,1.8810280520810734,1.1272532332078318,null,0,3.9987204094689699,7.9974408189379398,11.99616122840691,15.99488163787588,19.993602047344851,23.99232245681382,27.991042866282786,31.989763275751759,35.988483685220729,39.987204094689702]
[0.5,100,80,50,30,3.9133979892332427,3.1267838737903055,1.9505628781814539,1.1688715163691983,null,null,3.7959989814978772,7.7932600582081157,11.790521134918354,15.78778221162859,19.785043288338827,23.782304365049065,27.779565441759303,31.776826518469541,35.774087595179779,39.771348671890017]
[1,100,80,50,30,{"$f":"waCEBTP(altitude,$A36,B36)","v":4.0579649606593398},{"$f":"waCEBTP(altitude,$A36,C36)","v":3.2421415836580243},{"$f":"waCEBTP(altitude,$A36,D36)","v":2.0223853990705241},{"$f":"waCEBTP(altitude,$A36,E36)","v":1.2118551377469011},null,null,3.5934254658906286,7.5892282746203374,11.585031083350048,15.58083389207976,19.576636700809466,23.57243950953918,27.568242318268886,31.564045126998597,35.559847935728307,39.555650744458013]
[1.5,100,80,50,30,4.2073031769899707,3.3612952784717463,2.0965608592635285,1.2562427603163084,null,null,3.3909997008235138,7.3853453051859779,11.379690909548442,15.374036513910905,19.36838211827337,23.362727722635832,27.357073326998304,31.351418931360765,35.345764535723234,39.340110140085692]
[2,100,80,50,30,4.361550595811809,3.4843539216902295,2.1731560614792671,1.3020739520634952,null,null,3.1887215247087983,7.181610987154075,11.174500449599353,15.167389912044628,19.160279374489907,23.153168836935183,27.146058299380464,31.138947761825737,35.131837224271017,39.124726686716294]
[2.5,100,80,50,30,4.5208486226604938,3.6114291474894036,2.2522393970408467,1.3493892025178504,null,null,2.9865907761942867,6.9780251580109089,10.969459539827529,14.960893921644152,18.952328303460771,22.943762685277392,26.935197067094016,30.926631448910634,34.918065830727258,38.909500212543875]
[3,100,80,50,30,4.6853421886035358,3.742635317715417,2.3338808768295936,1.3982299395271625,null,null,2.7846072941628979,6.774587655479559,10.76456801679622,14.754548378112881,18.744528739429541,22.734509100746202,26.724489462062863,30.714469823379524,34.704450184696185,38.694430546012846]
[3.5,100,80,50,30,4.8551798298077227,3.8780895801459496,2.4181521628087848,1.4486385462808868,null,null,2.5827709177322347,6.5712983175194859,10.559825717306738,14.548353117093987,18.536880516881237,22.525407916668492,26.513935316455743,30.502462716242992,34.490990116030247,38.479517515817498]
[4,100,80,50,30,5.0305137691688371,4.0179119281075293,2.5051266001346688,1.5006583785876084,null,null,2.3810814862541587,6.3681569823260915,10.355232478398024,14.342307974469957,18.329383470541892,22.316458966613823,26.303534462685754,30.290609958757685,34.277685454829623,38.264760950901554]
[4.5,100,80,50,30,5.2115000000853042,4.1622252614989002,2.5948792498730904,1.5543337824130117,null,null,2.1795388393143611,6.1651634883302897,10.150788137346218,14.136412786362147,18.122037435378076,22.107662084394004,26.093286733409936,30.078911382425865,34.06453603144179,38.050160680457722]
[5,100,80,50,30,5.3982983724613822,4.3111554492728876,2.6874869223409128,1.609710111684989,null,null,1.9781428167319408,5.9623176741980846,9.9464925316642283,13.930667389130374,17.914842246596518,21.899017104062661,25.883191961528805,29.867366818994952,33.851541676461096,37.83571653392724]
[5.5,100,80,50,30,5.5910726810297078,4.4648313934317345,2.7830282110923674,1.6668337463728762,null,null,1.7768932585589781,5.7596193788301377,9.7423454991012957,13.725071619372457,17.707797739643613,21.690523859914773,25.673249980185936,29.655976100457096,33.638702220728256,37.621428340999415]
[6,100,80,50,30,5.7899907560873656,4.6233850945935169,2.8815835275713901,1.7257521108481131,null,null,1.575790005080111,5.5570684413613414,9.5383468776425708,13.519625313923802,17.500903750205033,21.482182186486263,25.463460622767496,29.444739059048725,33.426017495329951,37.407295931611188]
[6.5,100,80,50,30,5.9952245567442759,4.7869517191900073,2.9832351364520417,1.7865136925340415,null,null,1.3748328968121148,5.3546647011603978,9.3344965055086835,13.314328309856968,17.294160114205251,21.273991918553538,25.253823722901821,29.2336555272501,33.213487331598387,37.193319135946673]
[7,100,80,50,30,6.2069502667874961,4.9556696683592145,3.0880671916901155,1.8491680608528851,null,null,1.1740217745034776,5.1524079978293926,9.1307942211553073,13.10918044448122,17.087566667807135,21.065952891133048,25.044339114458964,29.022725337784877,33.00111156111079,36.979497784436703]
[7.5,100,80,50,30,6.4253483932700881,5.1296806485988791,3.1961657733101538,1.9137658864783813,null,null,0.97335647913398127,4.9502981712033627,8.9272398632727441,12.904181555342124,16.881123247411505,20.858064939480883,24.835006631550268,28.811948323619653,32.788890015689034,36.765831707758416]
[8,100,80,50,30,6.6506038679384858,5.3091297442503071,3.3076189249531973,1.980358960902926,null,null,0.77283685191428209,4.7483350613498878,8.7238332707854944,12.699331480221101,16.674829689656704,20.650327899092314,24.625826108527921,28.601324317963524,32.576822527399131,36.552320736834737]
[8.5,100,80,50,30,6.8829061516178847,5.4941654918852709,3.4225166922118042,2.0490002163285421,null,null,0.57246273428549055,4.5465185085686599,8.5205742828518289,12.494630057134998,16.468685831418167,20.442741605701336,24.416797379984505,28.390853154267674,32.364908928550847,36.338964702834012]
[9,100,80,50,30,7.1224493416809427,5.6849399566721193,3.5409511617800655,2.1197437458913897,null,null,0.37223396791875568,4.3448483533910629,8.3174627388633713,12.29007712433568,16.262691509807983,20.235305895280295,24.207920280752599,28.180534666224904,32.153149051697213,36.125763437169518]
[9.5,100,80,50,30,7.3694322827312408,5.8816088108008406,3.6630165014476579,2.19264482423003,null,null,0.17215039471484406,4.1433244365797544,8.1144984784446645,12.085672520309576,16.056846562174488,20.028020604039394,23.999194645904307,27.970368687769216,31.941542729634126,35.912716771499035]
[10,100,80,50,30,7.6240586806393527,6.084331414050653,3.7888090009682966,2.267759928408124,null,null,null,3.9419465991282463,7.9116813414527618,11.88141608377728,15.851150826101795,19.820885568426313,23.790620310750832,27.760355053075351,31.730089795399866,35.699824537724382]
[10.5,100,80,50,30,7.8865372200760531,6.2932708965875435,3.918427113834321,2.3451467592027271,null,null,null,3.7407146822604851,7.7090111679767999,11.677307653693115,15.645604139409432,19.613900625125748,23.582197110842063,27.550493596558379,31.518790082274691,35.487086567991007]
[11,100,80,50,30,8.1570816856943331,6.5085942440834312,4.051971499990632,2.4248642627698844,null,null,null,3.5396285274304362,7.5064877983375693,11.473347069244705,15.440206340151837,19.407065611058968,23.373924881966104,27.340784152873237,31.30764342378037,35.274502694687499]
[11.5,100,80,50,30,8.43591108711923,6.7304723852528427,4.1895450695226604,2.5069726526997398,null,null,null,3.3386879763216664,7.3041110730871095,11.269534169852554,15.234957266617997,19.200380363383442,23.165803460148886,27.131226556914328,31.096649653679773,35.062072750445218]
[12,100,80,50,30,8.7232497879123052,6.9590802819075881,4.3312530273546521,2.5915334324739532,null,null,null,3.13789287084693,7.1018808330082859,11.065868795169644,15.029856757330998,18.993844719492355,22.957832681653709,26.921820643815067,30.885808605976422,34.849796568137783]
[12.5,100,80,50,30,9.0193276386857839,7.1945970216346611,4.4772029189961824,2.678609418338779,null,null,null,2.9372430531477542,6.8997969191143698,10.862350785080986,14.824904651047602,18.787458517014215,22.750012382980831,26.712566248947446,30.675120114914062,34.637673980880678]
[13,100,80,50,30,9.3243801145499248,7.4372059132074888,4.6275046773764767,2.7682647626077617,null,null,null,2.7367383655940221,6.6978591726486192,10.658979979703217,14.620100786757813,18.581221593812412,22.54234240086701,26.503463207921609,30.464584014976207,34.425704822030809]
[13.5,100,80,50,30,9.6386484570862656,7.6870945848459575,4.7822706708079625,2.860564977408635,null,null,null,2.5363786507835635,6.4960674350838739,10.455756219384183,14.415445003684491,18.375133787984801,22.334822572285109,26.294511356585421,30.254200140885729,34.213888925186033]
[14,100,80,50,30,9.9623798210488665,7.9444550854460143,4.9416157521222468,2.9555769588896448,null,null,null,2.3361637515417417,6.2944215481221235,10.252679344702505,14.210937141282889,18.169194937863271,22.127452734443651,26.085710531024031,30.043968327604418,34.002226124184801]
[14.5,100,80,50,30,10.295827426005651,8.2094839889053812,5.1056573090236999,3.0533690119011911,null,null,null,2.1360935109210435,6.0929213536941154,10.049749196467186,14.006577039240256,17.963404882013329,21.920232724786398,25.877060567559472,29.833888410332541,33.790716253105614]
[15,100,80,50,30,10.639250713142451,8.4823825016779075,5.2745153157077809,3.1540108751693698,null,null,null,1.9361677722006658,5.8915666939589197,9.8469656157171741,13.802364537475428,17.757763459233683,21.713162380991935,25.668561302750184,29.623960224508441,33.579359146266697]
[15.5,100,80,50,30,10.992915507463445,8.7633565736953827,5.4483123857933844,3.2575737469787316,null,null,null,1.7363863788861118,5.690357411303534,9.6443284437209567,13.598299476138378,17.5522705085558,21.506241540973225,25.460212573390645,29.41418360580807,33.368154638225491]
[16,100,80,50,30,11.357094185633272,9.0526170128021608,5.6271738266206066,3.3641303113822989,null,null,null,1.5367491747087771,5.4892933483424615,9.4418375219761455,13.394381695609832,17.346925869243517,21.2994700428772,25.252014216510887,29.20455839014457,33.157102563778253]
[16.5,100,80,50,30,11.732065849718408,9.3503796028549324,5.8112276949676698,3.4737547649576777,null,null,null,1.3372560036255472,5.2883743479173075,9.2394926922090654,13.190611036500826,17.141729380792587,21.092847725084347,25.043966069376108,28.995084413667868,32.946202757959625]
[17,100,80,50,30,{"$f":"waCEBTP(altitude,$A68,B68)","v":12.118116507098261},{"$f":"waCEBTP(altitude,$A68,C68)","v":9.6568652256471808},{"$f":"waCEBTP(altitude,$A68,D68)","v":6.0006048542430399},{"$f":"waCEBTP(altitude,$A68,E68)","v":3.586522844128889},null,null,null,1.1379067098183853,5.0876002530963618,9.0372937963743389,12.986987339652314,16.936680882930293,20.88637442620827,24.836067969486248,28.785761512764225,32.735455056042206]
[17.5,100,80,50,30,12.515539256830047,9.9722999868254529,6.1954390332112839,3.7025118530743812,null,null,null,{"$f":"(20-1.007*$A69)/(2500.8+1.826*$A69)*1000","v":0.93870113769393448},{"$f":"(30-1.007*$A69)/(2500.8+1.826*$A69)*1000","v":4.886970907174204},{"$f":"(40-1.007*$A69)/(2500.8+1.826*$A69)*1000","v":8.8352406766544735},{"$f":"(50-1.007*$A69)/(2500.8+1.826*$A69)*1000","v":12.783510446134741},{"$f":"(60-1.007*$A69)/(2500.8+1.826*$A69)*1000","v":16.731780215615011},{"$f":"(70-1.007*$A69)/(2500.8+1.826*$A69)*1000","v":20.68004998509528},{"$f":"(80-1.007*$A69)/(2500.8+1.826*$A69)*1000","v":24.62831975457555},{"$f":"(90-1.007*$A69)/(2500.8+1.826*$A69)*1000","v":28.576589524055819},{"$f":"(100-1.007*$A69)/(2500.8+1.826*$A69)*1000","v":32.524859293536089}]
[18,100,80,50,30,12.924634482765939,10.296915345972661,6.3958668863138115,3.8218006922425602,null,null,null,{"$f":"(20-1.007*$A70)/(2500.8+1.826*$A70)*1000","v":0.73963913188310471},4.6864861536712787,8.6333331754594518,12.580180197247628,16.527027219035798,20.473874240823974,24.420721262612151,28.367568284400321,32.314415306188501]
[18.5,100,80,50,30,13.345710053735884,10.630948251041866,6.6020280556482387,3.9444698874970361,null,null,null,{"$f":"(20-1.007*$A71)/(2500.8+1.826*$A71)*1000","v":0.54072053724067348},4.4861458363335016,8.4315711354263296,12.376996434519159,16.322421733611986,20.267847032704818,24.213272331797643,28.158697630890472,32.104122929983298]
[19,100,80,50,30,13.779081531125799,10.974641277333042,6.8140652346730528,4.0706016199147861,null,null,null,{"$f":"(20-1.007*$A72)/(2500.8+1.826*$A72)*1000","v":0.34194519884488023},4.2859497991318456,8.229954399418812,12.173958999705777,16.117963599992745,20.061968200279708,24.005972800566674,27.949977400853641,31.893982001140603]
[19.5,100,80,50,30,14.225072384197258,11.328242771214306,7.0321242337070284,4.2002797562612892,null,null,null,{"$f":"(20-1.007*$A73)/(2500.8+1.826*$A73)*1000","v":0.14331296199703042},4.0858978862619448,8.0284828105268584,11.971067734791774,15.913652659056687,19.856237583321604,23.798822507586518,27.741407431851432,31.683992356116345]
[20,100,80,50,30,14.684014213512951,11.692006998799151,7.2563540472960435,4.3335898801678017,null,null,null,null,3.8859899421436803,7.8271562120662761,11.76832248198887,15.709488751911465,19.650655021834059,23.591821291756656,27.532987561679249,31.474153831601846]
[20.5,100,80,50,30,15.156246982850728,12.066194299801209,7.4869069235230086,4.470619324036913,null,null,null,null,3.6862258114207793,7.6259744475782956,11.565723083735811,15.505471719893325,19.445220356050839,23.384968992208357,27.324717628365871,31.264466264523389]
[21,100,80,50,30,15.642119260009006,12.451071246799069,7.7239384353400684,4.6114572017036135,null,null,null,null,3.4866053389604224,7.4249373608291922,11.363269382697963,15.301601404566732,19.239933426435503,23.178265448304273,27.116597470173044,31.054929492041811]
[21.5,100,80,50,30,16.141988466927153,12.846910810154851,7.9676075540055695,4.7561944418802264,null,null,null,null,3.2871283698528271,7.2240447958098617,11.160961221766895,15.097877647723932,19.034794073680967,22.971710499638,26.908626925595037,30.84554335155207]
[22,100,80,50,30,16.656221139566853,13.253992528842366,8.2180767247120983,4.9049238224147365,null,null,null,null,3.0877947494108566,7.0232965967354231,10.95879844405999,14.894300291384557,18.829802138709123,22.76530398603369,26.70080583335826,30.636307680682823]
[22.5,100,80,50,30,17.18519319802369,13.672602687453132,8.4755119444955174,5.0577400053932182,null,null,null,null,2.8886043231696164,6.8226926080448171,10.756780892920018,14.690869177795218,18.62495746267042,22.559045747545618,26.493134032420819,30.427222317296021]
[23,100,80,50,30,17.729290227363169,14.103034499661909,8.7400828425190298,5.2147395731183526,null,null,null,null,2.6895569368860608,6.6222326744004052,10.554908411914749,14.487584149429091,18.420259886943438,22.352935624457782,26.285611361972123,30.218287099486467]
[23.5,100,80,50,30,18.288907769701567,14.545588298447315,9.0119627628303736,5.3760210649972935,null,null,null,null,2.490652436538586,6.421916640687563,10.35318084483654,14.284445048985518,18.215709253134495,22.146973457283472,26.078237661432446,30.009501865581424]
[24,100,80,50,30,18.864451628080058,15.000571733377921,9.2913288496946507,5.5416850153735364,null,null,null,null,2.2918906683266371,6.2217443520142854,10.151598035701934,14.081451719389582,18.01130540307723,21.941159086764877,25.871012770452527,29.800866454140177]
[24.5,100,80,50,30,19.456338182709686,15.468299975289668,9.5783621356097584,5.7118339923387769,null,null,null,null,2.0932714786703164,6.021715653710789,9.9501598287512607,13.878604003791736,17.807048178832208,21.735492353872679,25.663936528913151,29.592380703953626]
[25,100,80,50,30,20.064994720196552,15.949095928697044,9.8732476321162768,5.8865726375623106,null,null,null,null,1.8947947142099795,5.8218303913291054,9.7488660684482316,13.675901745567359,17.602937422686484,21.529973099805609,25.457008776924734,29.384044454043863]
[25.5,100,80,50,30,20.690859776389249,16.443290452297596,10.1761744235185,6.0660077071769258,null,null,null,null,1.6964602218058453,5.6220884106426929,9.547716599479541,13.473344788316387,17.398972977153235,21.324601165990082,25.250229354826931,29.175857543663778]
[26,100,80,50,30,21.334383493526175,16.951222587947818,10.487335763638619,6.2502481137619048,null,null,null,null,1.4982678485376,5.4224895576460321,9.3467112667544647,13.270932975862895,17.195154684971328,21.119376394079758,25.043598103188192,28.967819812296625]
[26.5,100,80,50,30,21.996027992397511,17.473239798507766,10.806929175731515,6.4394049694653619,null,null,null,null,1.3002174417040095,5.2230336785542377,9.1458499154044688,13.068666152254696,16.991482389104927,20.914298625955155,24.837114862805382,28.759931099655617]
[27,100,80,50,30,22.67626776027646,18.009698214972136,11.135156555693294,6.6335916303098443,null,null,null,null,1.102308848822519,5.0237206198026598,8.9451323907827991,12.866544161762942,16.787955932743085,20.709367703723224,24.630779474703367,28.552191245683506]
[27.5,100,80,50,30,23.375590055416396,18.560962893327257,11.472224278702772,6.8329237417268951,null,null,null,null,0.90454191762886704,4.8245502280464851,8.7445585384641031,12.664566848881721,16.584575159299337,20.504583469716955,24.424591780134573,28.344600090552191]
[28,100,80,50,30,24.09449532895561,19.127408081596304,11.818343309441365,7.0375192853681661,null,null,null,null,0.7069164960766926,4.6255223501603497,8.5441282042440072,12.462734058327664,16.38133991241132,20.299945766494979,24.218551620578634,28.137157474662292]
[28.5,100,80,50,30,24.833497665118749,19.709417497559151,12.173729316043495,7.2474986272425284,null,null,null,null,0.50943243233715019,4.42663683323795,8.3438412341387487,12.261045635039551,16.178250035940348,20.095454436841148,24.012658837741949,27.929863238642746]
[29,100,80,50,30,25.593125240655095,20.307384617659153,12.538602787936481,7.4629845672306958,null,null,null,null,0.3120895747985139,4.227893524591642,8.1436974743847692,12.059501424177896,15.975305373971024,19.891109323764152,23.806913273557281,27.722717223350404]
[29.5,100,80,50,30,26.373920804507545,20.921712977636002,12.91318915773628,7.6841023900309109,null,null,null,null,0.11488777206579237,4.0292922717520527,7.9436967714383124,11.858101271124571,15.772505770810831,19.686910270497091,23.601314770183354,27.51571926986961]
[30,100,80,50,30,27.176442178763935,21.552816485452816,13.29771892737296,7.9109799175914777,null,null,null,null,null,3.8308329224676987,7.74383897197505,11.656845021482402,15.569851070989756,19.482857120497108,23.395863170004461,27.308869219511813]
[30.5,100,80,50,30,28.001262782003387,22.201119747115985,13.692427798627909,8.1437475630881053,null,null,null,null,null,3.6325153247045865,7.5441239228896775,11.455732521074768,15.36734111925986,19.278949717444952,23.190558315630042,27.102166913815136]
[31,100,80,50,30,28.848972176216026,22.867058406018757,14.097556808273207,8.3825383865064929,null,null,null,null,null,3.4343393266458291,7.3445514712955244,11.254763615945219,15.164975760594913,19.075187905244608,22.985400049894302,26.895612194543997]
[31.5,100,80,50,30,29.720176638543787,23.551079496473747,14.513352468012428,8.6274881518929725,null,null,null,null,null,3.2363047766912576,7.1451214645241654,11.053938152357075,14.962754840189982,18.871571528022891,22.780388215855798,26.689204903688704]
[32,100,80,50,30,30.615499759164621,24.253641812136095,14.940066909431504,8.8787353863386222,null,null,null,null,null,3.0384115234570386,6.9458337501250389,10.85325597679304,14.760678203461039,18.668100430129041,22.575522656797041,26.482944883465045]
[32.5,100,80,50,30,31.535583066721816,24.975216290057691,15.377958034178121,9.1364214407649769,null,null,null,null,null,2.8406594157752787,6.7466881758650397,10.6527169359548,14.558745696044561,18.464774456134322,22.370803216224083,26.276831976313847]
[33,100,80,50,30,{"$f":"waCEBTP(altitude,$A100,B100)","v":32.481086682784778},{"$f":"waCEBTP(altitude,$A100,C100)","v":25.716286411153863},{"$f":"waCEBTP(altitude,$A100,D100)","v":15.827289669598363},{"$f":"waCEBTP(altitude,$A100,E100)","v":9.4006905525821853},null,null,null,null,null,2.6430483026936549,6.5476845897281528,10.452320876762654,14.356957163797151,18.261593450831651,22.16622973786615,26.070866024900649]
[33.5,100,80,50,30,33.452690006918687,26.477348617907943,16.288331730070354,9.6716899102935088,null,null,null,null,null,2.4455780334750092,6.3488228399150515,10.252067646355092,14.155312452795135,18.058557259235176,21.961802065675219,25.865046872115258]
[34,100,80,50,30,34.451092434036759,27.258912750185047,16.761360384285876,9.9495697201229341,null,null,null,null,null,2.2482484575969885,6.1501027748427166,10.051957092088445,13.953811409334172,17.8556657265799,21.757520043825625,25.659374361071354]
[34.5,100,80,50,30,35.477014105813431,28.061502500076617,17.246658228743314,10.234483274746095,null,null,null,null,null,2.0510594247516498,5.9515242431440578,9.8519890615364663,13.752453879928872,17.65291869832128,21.553383516713687,25.453848335106095]
[35,100,80,50,30,36.531196698046948,28.885655886749159,17.744514467727733,10.526587024207798,null,null,null,null,null,1.8540107848450713,5.7530870936675109,9.6521634024899505,13.551239711312391,17.450316020134832,21.349392328957268,25.248468637779705]
[35.5,100,80,50,30,37.614404245979344,29.731925752327051,18.255225100067417,10.826040649113095,null,null,null,null,null,1.6571023879969922,5.5547911754766801,9.4524799629563692,13.350168750436056,17.247857537915745,21.145546325395433,25.04323511287512]
[36,100,80,50,30,38.72742400970904,30.600880279899062,18.779093112970425,11.133007136182426,null,null,null,null,null,1.4603340845404096,5.3566363378499284,9.2529385911594488,13.149240844468967,17.045543097778488,20.941845351088006,24.838147604397523]
[36.5,100,80,50,30,39.871067381967961,31.49310353480158,19.316428683259527,11.447652856265195,null,null,null,null,null,1.2637057250212183,5.1586224302800181,9.0535391355388182,12.948455840797617,16.843372546056418,20.738289251315216,24.633205956574017]
[37,100,80,50,30,41.046170840681661,32.409196030399698,19.867549386339721,11.770147644910095,null,null,null,null,null,1.0672171601978251,4.9607493024737188,8.8542814447496117,12.747813587025506,16.641345729301403,20.534877871577297,24.428410013853192]
[37.5,100,80,50,30,42.253596948888259,33.349775319659521,20.432780413249141,12.100664885594712,null,null,null,null,null,0.8708682410407621,4.7630168043514232,8.6551653676620841,12.547313930972747,16.439462494283408,20.331611057594067,24.22375962090473]
[38,100,80,50,30,43.494235404761184,34.315476613882645,21.012454796161808,12.439381595721329,null,null,null,null,null,0.67465881873232691,4.5654247860467798,8.4561907533612342,12.346956720675687,16.237722687990139,20.12848865530459,24.019254622619048]
[38.5,100,80,50,30,44.769004144662034,35.30695343005582,21.606913642729172,12.786478515490355,null,null,null,null,null,0.478588744666198,4.3679730979063081,8.2573574511464169,12.146741804386528,16.03612615762664,19.925510510866747,23.814894864106854]
[39,100,80,50,30,46.07885050234573,36.324878268357757,22.216506379667162,13.142140199767743,null,null,null,null,null,0.28265787044705193,4.1706615904890114,8.0586653105309711,11.946669030572929,15.834672750614887,19.722676470656847,23.610680190698805]
[39.5,100,80,50,30,47.424752427649608,37.369943321458763,22.841591006016166,13.506555113067636,null,null,null,null,null,8.6866047890204953E-2,3.973490114566018,7.8601141812418298,11.746738247917644,15.633362314593457,19.51998638126927,23.406610447945081]
[40,100,80,50,30,48.8077197682247,38.442861217349808,23.482534356523207,13.87991572777684,null,null,null,null,null,null,3.7764585211201958,7.6617039132191609,11.546949305318126,15.43219469741709,19.317440089516055,23.202685481615021]
[40.5,100,80,50,30,50.228795618111505,39.544365797546185,24.139712375619276,14.262418625753329,null,null,null,null,null,null,3.5795666613457691,7.4634343566159558,11.347302051886142,15.231169747156329,19.115037442426516,22.998905137696706]
[41,100,80,50,30,51.689057737224701,40.675212932625932,24.813510402488973,14.654264603436664,null,null,null,null,null,null,3.3828143866479583,7.2653053617976857,11.147796336947414,15.030287312097142,18.912778287246869,22.795269262396598]
[41.5,100,80,50,30,53.189620046094817,41.836181377187081,25.504323467755903,15.055658780614346,null,null,null,null,null,null,3.1862015486426016,7.0673167793419118,10.948432010041222,14.829547240740533,18.710662471439846,22.591777702139158]
[42,100,80,50,30,54.731634200521306,43.028073666441244,26.212556602335042,15.466810712994612,null,null,null,null,null,null,2.9897279991557695,6.8694684600378979,10.749208920920026,14.628949381802155,18.508689842684284,22.388430303566413]
[42.5,100,80,50,30,56.316291251120802,44.251717056802406,26.938625159032394,15.887934508742733,null,null,null,null,null,null,2.7933935902234159,6.6717602548862596,10.550126919549104,14.428493584211946,18.306860248874791,22.185226913537633]
[43,100,80,50,30,57.944823393112763,45.507964512983818,27.68295514750368,16.319248949145209,null,null,null,null,null,null,2.5971981740909822,6.4741920150985663,10.35118585610615,14.228179697113733,18.105173538121317,21.982167379128903]
[43.5,100,80,50,30,59.618505812069209,46.797695744278606,28.445983583216275,16.760977613573264,null,null,null,null,null,null,2.4011416032130466,6.2767635920969873,10.152385580980928,14.028007569864869,17.903629558748808,21.77925154763275]
[44,100,80,50,30,61.338658631775147,48.121818292877634,29.228158851094502,17.213349008925384,null,null,null,null,null,null,2.2052237302529445,6.0794748375139109,9.9537259447748756,13.827977052035843,17.702228159296808,21.576479266557776]
[44.5,100,80,50,30,63.106648970796911,49.481268677265852,30.029941084564591,17.676596703736305,null,null,null,null,null,null,2.0094444080823948,5.8823256031915649,9.7552067983007351,13.628087993409904,17.500969188519075,21.373850383628248]
[45,100,80,50,30,64.923893114847814,50.877013593943886,30.851802560755974,18.150959467148915,null,null,null,null,null,null,1.8138034897811441,5.6853157411816637,9.556827992582182,13.428340243982701,17.29985249538322,21.171364746783741]
[45.5,100,80,50,30,66.791858812571718,52.310051180939773,31.694228112657203,18.636681412954388,null,null,null,null,null,null,1.6183008286365932,5.4884451037450246,9.3585893788534555,13.228733653961887,17.098877929070319,20.969022204178749]
[46,100,80,50,30,68.712067702942676,53.781412346812637,32.557715559069464,19.134012148915524,null,null,null,null,null,null,1.4229362781434218,5.2917135433511984,9.1604908085589738,13.029268073766749,16.898045338974526,20.766822604182302]
[46.5,100,80,50,30,70.68609788310664,55.292162169104628,33.442776153248388,19.643206931598307,null,null,null,null,null,null,1.2277096920032384,5.0951209126781087,8.9625321333529797,12.829943354027851,16.697354574702722,20.564765795377593]
[47,100,80,50,30,72.715586626172239,56.843401366471582,34.349935051175251,20.164526826947384,null,null,null,null,null,null,1.0326209241242077,4.8986670646116846,8.7647132050991612,12.63075934558664,16.496805486074116,20.362851626561593]
[47.5,100,80,50,30,74.802233259199923,58.436267849019281,35.279731800452488,20.698238876852173,null,null,null,null,null,null,0.83766982862067718,4.7023518522454779,8.5670338758702798,12.431715899495078,16.29639792311988,20.161079946744682]
[48,100,80,50,30,76.947802212446945,60.071938351692502,36.232720850876184,21.244616271962371,null,null,null,null,null,null,0.64285625981283046,4.5061751288803169,8.3694939979478047,12.232812867015292,16.096131736082778,19.959450605150266]
[48.5,100,80,50,30,79.154126251804286,61.751630155907911,37.209472087798758,21.803938531023814,null,null,null,null,null,null,0.44818007222631601,4.3101367480239352,8.1720934238215541,12.034050099619174,15.896006775416794,19.757963451214412]
[49,100,80,50,30,81.423109907323067,63.476602904997648,38.210571389460824,22.37649168701893,null,null,null,null,null,null,0.25364112059187693,4.114236563390592,7.974832006189307,11.835427448988021,15.696022891786738,19.556618334585451]
[49.5,100,80,50,30,83.756733111773698,65.24816051943175,39.23662120954021,22.962568480409679,null,null,null,null,null,null,{"$f":"(50-1.007*$A133)/(2500.8+1.826*$A133)*1000","v":5.9239259845008545E-2},{"$f":"(60-1.007*$A133)/(2500.8+1.826*$A133)*1000","v":3.9184744289007343},{"$f":"(70-1.007*$A133)/(2500.8+1.826*$A133)*1000","v":7.7777095979564601},{"$f":"(80-1.007*$A133)/(2500.8+1.826*$A133)*1000","v":11.636944767012187},{"$f":"(90-1.007*$A133)/(2500.8+1.826*$A133)*1000","v":15.496179936067911},{"$f":"(100-1.007*$A133)/(2500.8+1.826*$A133)*1000","v":19.355415105123637}]
[50,100,80,50,30,86.157055064327437,67.067653218227846,40.288241186240995,23.562468559795867,null,null,null,null,null,null,null,{"$f":"(60-1.007*$A134)/(2500.8+1.826*$A134)*1000","v":3.7228501986806082},{"$f":"(70-1.007*$A134)/(2500.8+1.826*$A134)*1000","v":7.580726052235641},{"$f":"(80-1.007*$A134)/(2500.8+1.826*$A134)*1000","v":11.438601905790673},{"$f":"(90-1.007*$A134)/(2500.8+1.826*$A134)*1000","v":15.296477759345704},{"$f":"(100-1.007*$A134)/(2500.8+1.826*$A134)*1000","v":19.154353612900735}]

{"sheet":"Liste","index":1,"n_rows":36,"n_cols":13,"rows_kept":36,"cut":false,"hidden":false,"merged":[[24,11,25,13],[27,8,27,9],[25,5,25,6],[26,5,26,6],[26,8,26,9],[26,2,26,3],[27,2,27,3],[8,2,8,3],[11,5,11,6],[16,2,16,3],[17,2,17,3],[13,8,13,9],[14,8,14,9],[9,2,9,3],[12,5,12,6],[1,8,1,9],[1,5,1,6],[1,2,1,3],[2,2,2,3],[2,5,2,6],[2,8,2,9]]}
[]
[]
[null,null,"Batterie chaude sèche",null,null,"Batterie chaude + humidificateur",null,null,"Batterie froide pour déshumidifier + batterie chaude"]
[null,null,"Te [°C]",null,null,"Te [°C]",8.1980000000000004,null,"Te [°C]"]
[null,null,"Ts [°C]",null,null,"Ts [°C]",22.222000000000001,null,"Ts [°C]"]
[null,null,"we [g/kgas]",null,null,"we [g/kgas]",4.9548868480710864,null,"we [g/kgas]"]
[null,null,"ws [g/kgas]",null,null,"ws [g/kgas]",6.933761196680158,null,"ws [g/kgas]"]
[null,null,null,null,null,"T_inter [°C]",22.222000000000001,null,"T_inter [°C]"]
[null,null,null,null,null,"w_inter [g/kgas]",4.9548868480710864,null,"w_inter [g/kgas]"]
[null,null,"Batterie froide sèche",null,null,"T_interHum [°C]",27.181860634427466]
[null,null,"Te [°C]"]
[null,null,"Ts [°C]"]
[null,null,"we [g/kgas]",null,null,"Batterie froide + humidificateur"]
[null,null,"ws [g/kgas]",null,null,"Te [°C]"]
[null,null,null,null,null,"Ts [°C]",null,null,"Batterie chaude + humidificateur + te < 3°"]
[null,null,null,null,null,"we [g/kgas]",null,null,"Te [°C]"]
[null,null,null,null,null,"ws [g/kgas]",null,null,"Ts [°C]"]
[null,null,"Batterie chaude sèche + te<3°",null,null,"T_inter [°C]",null,null,"we [g/kgas]"]
[null,null,"Te [°C]",null,null,"w_inter [g/kgas]",null,null,"ws [g/kgas]"]
[null,null,"Ts [°C]",null,null,"T_infini [°C]",null,null,"T_inter [°C]"]
[null,null,"we [g/kgas]",null,null,"w_infini [g/kgas]",null,null,"w_inter [g/kgas]"]
[null,null,"ws [g/kgas]",null,null,"T_interHum [°C]",null,null,"Te3 [°C]"]
[null,null,"Te3 [°C]",null,null,"w_interHum [g/kgas]",null,null,"we3 [g/kgas]"]
[null,null,"we3 [g/kgas]",null,null,null,null,null,"T_interHum [°C]"]
[null,null,null,null,null,null,null,null,null,null,null,"MANUEL D'UTILISATION"]
[]
[null,null,null,null,null,"Succession d'humificateurs"]
[null,null,"Hum Pulv eau + Batterie froide",null,null,"Te [°C]",null,null,"Batterie chaude + déshumidificateur",null,null,"Récapitulatif soufflage"]
[null,null,"Te [°C]",null,null,"Ts [°C]",null,null,"Te [°C]",null,null,"T soufflage",22.222014461732073]
[null,null,"Ts [°C]",null,null,"we [g/kgas]",null,null,"Ts [°C]",null,null,"T mélange",8.1975739578664264]
[null,null,"we [g/kgas]",null,null,"ws [g/kgas]",null,null,"we [g/kgas]",null,null,"T extérieur",-9]
[null,null,"ws [g/kgas]",null,null,"T_inter [°C]",null,null,"ws [g/kgas]",null,null,"T intérieur",12]
[null,null,"T_inter[°C]",null,null,"w_inter [g/kgas]",null,null,"T_inter [°C]",null,null,"w soufflage",6.8227254435534128]
[null,null,"w_inter [g/kgas]",null,null,null,null,null,"w_inter [g/kgas]",null,null,"w mélange",4.9401230785497479]
[null,null,null,null,null,null,null,null,null,null,null,"w extérieur",1.5387474927473868]
[null,null,null,null,null,null,null,null,null,null,null,"w intérieur",5.6783292691214582]

{"sheet":"Resultats","index":3,"n_rows":40,"n_cols":4,"rows_kept":40,"cut":false,"hidden":false,"merged":[[36,2,36,3],[38,2,38,3],[22,2,22,3],[1,2,1,3],[2,2,2,3],[9,2,9,3],[12,2,12,3],[15,2,15,3],[18,2,18,3],[26,2,26,3],[30,2,30,3],[34,2,34,3]]}
[]
[null,null,"Résultats\nDimensionnement d'une CTA"]
[null,null,"Données d'entrées"]
[null,null,"Température d'entrée [°C]",8.1980000000000004]
[null,null,"Humidité relative d'entrée [%]",73.03]
[null,null,"Humidité spécifique d'entrée [kg/kgas]",5.0000000000000001E-3]
[null,null,"Température de sortie [°C]",22.222000000000001]
[null,null,"Humidité relative de sortie [%]",40.79]
[null,null,"Humidité spécifique de sortie [kg/kgas]",7.0000000000000001E-3]
[null,null,"Batterie de préchauffage"]
[null,null,"Puissance [kW]",0]
[null,null,"Efficacité [%]",0]
[null,null,"Batterie chaude"]
[null,null,"Puissance [kW]",221.91]
[null,null,"Efficacité [%]",22.69]
[null,null,"Batterie chaude\nAssociée avec un humidificateur à injection d'eau"]
[null,null,"Puissance [kW]",300.39999999999998]
[null,null,"Efficacité [%]",31.75]
[null,null,"Batterie de froide"]
[null,null,"Puissance [kW]",0]
[null,null,"Efficacité [%]",0]
[null,null,"Débit d'eau condensé [kg/h]",0]
[null,null,"Batterie de froide \nAssociée avec un humidificateur à injection d'eau"]
[null,null,"Puissance [kW]",0]
[null,null,"Efficacité [%]",0]
[null,null,"Débit d'eau condensé [kg/h]",0]
[null,null,"Calcul intermédiaire par injection de vapeur"]
[null,null,"Température intermédiaire [°C]",0]
[null,null,"Humidité spécifique intermédiaire [kg/kgas]",0]
[null,null,"Enthalpie spécifique [kJ/kgas]",0]
[null,null,"Calcul intermédiaire par pulvérisation à eau"]
[null,null,"Température intermédiaire [°C]",0]
[null,null,"Humidité spécifique intermédiaire [kg/kgas]",0]
[null,null,"Enthalpie spécifique [kJ/kgas]",0]
[null,null,"Humidificateur par injection de vapeur"]
[null,null,"Masse d'eau vaporisée [kg/h]",111.06]
[null,null,"Humidificateur par pulvérisation d'eau"]
[null,null,"Masse d'eau [kg/h]",111.06]
[null,null,"Ventilateur de sortie"]
[null,null,"Puissance [kW]",5.6]